## ADM Review Comments (hidden)
ADM Reviewer | Date | Worksheet | Cell Location | Issue | Resolution
Amir Makhzani | 2023-10-30 | Air Compressor | Column O | This is not a major issue but the delta CLF set to be defult value , in some cases this value can be obtained from data sheet or namplate for baseline and as built. ADM will likely use site-specific data collection, which may cause some differences between reported and evaluated impacts.
Amir Makhzani | 2023-10-30 | Cycling Dryer | Column E | This is not a significant issue but most of the parameters are set to be defult value however some of them can be obtain from data sheet or nameplate and it is better to use actual value (EDC data gathering) rather than defult values. ADM will likely use site-specific data collection, which may cause some differences between reported and evaluated impacts.
Amir Makhzani | 2023-10-30 | ACondensate Drains | Column G | Add option of unknown to compressor control type which returns 0.27 as a kW/CFM from TRM table 3-187

## Instructions
| Instructions |  | Worksheet Version | 5.1
Energy Solutions For Business Programs
This tool is provided to calculate energy and demand savings relating to compressed air measures recognized in Pennsylvania.
Project Summary
Enter the building's operating schedule in 24hr time format.
Air Compressor Replacement
This measure is for a new compressor installation or replacement of existing compressor in a single compressor system only. The full load brake horspower cannot exceed 40 HP and must match the BHP of the replacement machine. The existing machine must have modulation controls.
Cycling Dryer
This measure is for cycling refrigerated thermal mass dryers. To be eligible, the replaced dryer must be a non-cycling refrigerated air dryer with a capacity of 600 cfm or less.
Air Nozzles
This measure is for air-entraining air nozzle replacement. To be eligible, the replaced nozzle must be a stationary air nozzle with an open copper tube of 1/8" or 1/4" diameter. The new nozzle, must use less than 15 CFM at 100 psi for industrial applications.
Condensate Drains
This measure is for no loss condensate drains. To be eligible, the replaced condensate drains must be operated by a solenoid and timer.
Air Tanks
This measure is for air tanks for load/no load compressors. To be eligible the installed air receiver must have pressure/flow controls to load/no load compressors. There must be a minimum ration of 4 gallons of storage per cfm.
White Cells | This cell requires an input for the calculator to operate properly
Yellow Cells | This cell is a default value from the TRM
Red Cells | The cell indicates a change from a default value and will require data to verify
Gray Cells | The cell is a calculation and requires no action
Blue Cells | The cell is a heading
Green Cells | The cell is a total of the column
Light Blue Cells | This cell is an overridable value
Heading Name |  | Description of Input
Building Name |  | The name of the facility
Building Schedule |  | The schedule the compressors run on
Full Load BHP |  | The full load brake horsepower of the machine
Number of Compressors |  | The number of compressors in the system
Horsepower of Compressors |  | The horspower of the compressors in the system
Nozzle Diameter |  | The diameter of the nozzles; baseline and new
Number of Nozzles Installed |  | The number of nozzles installed
Compressor Control Type |  | The control type on the compressor
Drain Oriface Diameter |  | The diameter of the drain oriface
System Pressure |  | The pressure the compressor system runs on
Number of Drains Installed |  | Number of drains installed
Compressor HP Range |  | The horsepower range the compressors operate in

## Methodology (hidden)
Calculator Methodology
Figure 1: PA TRM Info on cycling dryers
Figure 2: Equations for cycling dryers
Figure 3: Variable Definitions
Figure 4: Air Entraining Nozzles information
Figure 5: Equation for air entraining nozzle
Figure 6: Variable Definitions
Figure 7: condensate drains information
Figure 8: Equations for compressed air calculations
Figure 9: Variable definitions for condensate drains
Figure 10: Air tank information
Figure 11: Air tank equations
Figure 12: air tank variable definitions
Figure 13: VSD information
Figure 14: VSD equations
Figure 15: Definitions
Figure 16: VSD Hours per Year, CF factors

## Project Summary
Deemed Compressed Air Savings
Building Operation Schedule
Please enter the building operational hours as On/Off times each day in 24-hr. format. The first column shows an example of a facility open 8am to 5pm on weekdays, and 24 hours on the weekends for reference.
| Example |  | <Input Name>
| On | Off | On | Off
Monday | 8 | 17
Tuesday | 8 | 17
Wednesday | 8 | 17
Thursday | 8 | 17
Friday | 8 | 17
Saturday | 0 | 24
Sunday | 0 | 24
Holidays Observed Annual | 8
Yearly Operating Weeks | 52
Unoccupied Peak Weeks | 0
Hours of Use | 4777 |  | 0
Coincidence Factor | 0.75 |  | 0
Estimated Annual kWh Savings |  |  | 0
Estimated Annual kW Savings |  |  | 0
Measure |  |  | Quantity | kWh | Peak kW | Incentive
Air Compressor |  |  | 0 | 0 | 0 | 0
Cycling Dryer |  |  | 0 | 0 | 0 | 0
Air Nozzle |  |  | 0 | 0 | 0 | 0
Condensate Drains |  |  | 0 | 0 | 0 | 0
Air Tanks |  |  | 0 | 0 | 0 | 0
Custom Coincidence Factor Calculations
|  |  | 14 | 15 | 16 | 17
Monday |  |  | 1 | 1 | 1 | 0 | Example
Tuesday |  |  | 1 | 1 | 1 | 0
Wednesday |  |  | 1 | 1 | 1 | 0
Thursday |  |  | 1 | 1 | 1 | 0
Friday |  |  | 1 | 1 | 1 | 0
CF |  |  | 0.75
Monday |  |  | 0 | 0 | 0 | 0 | <Input Name>
Tuesday |  |  | 0 | 0 | 0 | 0
Wednesday |  |  | 0 | 0 | 0 | 0
Thursday |  |  | 0 | 0 | 0 | 0
Friday |  |  | 0 | 0 | 0 | 0
CF |  |  | 0

## Air Compressor
Variable Speed Drive Air Compressor
Variable-Speed Drive (VSD) Air Compressors use a variable speed drive on the motor to match motor output to the load, resulting in greater efficiency than fixed-speed air compressors. Baseline compressors choke off inlet air to modulate the compressor output, resulting in increased energy consumption and peak demand. To qualify for this measure, a participating commercial or industrial establishment must install or retrofit a ≤ 200 HP compressor with variable speed control. Projects involving compressors larger than 200 HP should be treated as custom projects.
Facility Information |  |  | Baseline Information |  |  |  |  | Proposed Information |  |  |  | Data Values | [5 empty] | Calulations
Line Item | Building Name | Building Schedule | Existing Manufacturer | Existing Model Number | Full Load BHP | Existing Control | Pressure (PSI) | New Manufacturer | New Model Number | Full Load BHP | Proposed Control | Facility HOU | kW factor | CLF_b | CLF_e | D CLF | CF | Annual kWh | Non Coincident Peak kW | Peak kW
1 | [9 empty] | 0 | Variable Speed Drive |  | 0.9 | 0 | 0.705 | -0.705 |  | 0 | 0 | 0
2 | [9 empty] | 0 | Variable Speed Drive |  | 0.9 | 0 | 0.705 | -0.705 |  | 0 | 0 | 0
3 | [9 empty] | 0 | Variable Speed Drive |  | 0.9 | 0 | 0.705 | -0.705 |  | 0 | 0 | 0
4 | [9 empty] | 0 | Variable Speed Drive |  | 0.9 | 0 | 0.705 | -0.705 |  | 0 | 0 | 0
5 | [9 empty] | 0 | Variable Speed Drive |  | 0.9 | 0 | 0.705 | -0.705 |  | 0 | 0 | 0
6 | [9 empty] | 0 | Variable Speed Drive |  | 0.9 | 0 | 0.705 | -0.705 |  | 0 | 0 | 0
7 | [9 empty] | 0 | Variable Speed Drive |  | 0.9 | 0 | 0.705 | -0.705 |  | 0 | 0 | 0
8 | [9 empty] | 0 | Variable Speed Drive |  | 0.9 | 0 | 0.705 | -0.705 |  | 0 | 0 | 0
| Baseline Compressor | <=40HP | 50-200HP
| Modulation with Blowdown | 0.89 | 0.863
| Load/No-Load w/ 1 Gallon/CFM | 0.909 | 0.887
| Load/No-Load w/ 3 Gallon/CFM | 0.831 | 0.811
| Load/No-Load w/ 5 Gallon/CFM | 0.806 | 0.786
| VSD Air Compressor | 0.705 | 0.658

## Cycling Dryer
Cycling Dryers
A Cycling Refrigerated Thermal Mass Dryer uses a thermal storage medium to store cooling capacity when the system is operated at partial loads allowing the dryer refrigerant compressor to cycle. This measure is targeted to customers with non-cycling (e.g., continuous) air dryer with a capacity of 600 cfm or below. The replacement of desiccant, deliquescent, heat-of-compression, membrane, or other types of dryers does not qualify under this measure. Efficient conditions are a cycling thermal mass dryer with a capacity of 600 cfm or below.
Facility Information |  |  | Data Inputs |  |  |  |  | Results
Line Item | Building Name | Building Schedule | Total Horsepower of Compressor(s) | Compressor Output CFM/HP (Default: 4) | kWdryer/CFMcomp (Default: 0.0087) | Chilled Coil Response Time Derate (Default: 0.925) | Average Compressor Operating Capacity (Default: 0.65) | Hours of Operation | Coincidence Factor | Non Coincident kW | Peak kW Savings | Annual kWh Savings
1 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
2 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
3 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
4 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
5 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
6 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
7 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
8 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
9 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
10 |  |  |  | 4 | 0.0087 | 0.925 | 0.65 | #N/A | #N/A | 0 | 0 | 0
Totals | [9 empty] | 0 | 0 | 0

## Air Nozzle
Entraining Air Nozzles
Air entraining air nozzles use compressed air to entrain and amplify atmospheric air into a stream, increasing pressure with minimal compressed air use. This decreases the compressor work necessary to provide the nozzles with compressed air. This measure is targeted to customers whose compressed air equipment uses stationary air nozzles in a production application with an open copper tube of 1/8” or 1/4” orifice diameter. Energy efficient conditions require replacement of an inefficient, non-air entraining air nozzle with an energy efficient air-entraining air nozzle that use less than 15 CFM at 100 psi for industrial applications.
Facility Information |  |  | Input Data | [7 empty] | Results
Line Item | Building Name | Building Schedule | Number of Nozzles Installed | Baseline Nozzle Diameter | Baseline Nozzle Air Mass Flow | Energy Efficient Nozzle Diameter | Energy Efficient Nozzle Air Mass Flow | Compressor Control Type | Ratio of Compressor kW/CFM | Percent of Hours when Nozzle is in Use (Default 5%, max 10%) | Hours of Operation | Coincidence Factor | Annual kWh Savings | Non Coincident kW | Peak kW Savings
1 | [9 empty] | 5% |  |  | 0 | 0 | 0
2 | [9 empty] | 5% |  |  | 0 | 0 | 0
3 | [9 empty] | 5% |  |  | 0 | 0 | 0
4 | [9 empty] | 5% |  |  | 0 | 0 | 0
5 | [9 empty] | 5% |  |  | 0 | 0 | 0
6 | [9 empty] | 5% |  |  | 0 | 0 | 0
7 | [9 empty] | 5% |  |  | 0 | 0 | 0
8 | [9 empty] | 5% |  |  | 0 | 0 | 0
9 | [9 empty] | 5% |  |  | 0 | 0 | 0
10 | [9 empty] | 5% |  |  | 0 | 0 | 0
Totals |  |  | 0 | [9 empty] | 0 | 0 | 0
Note on F8: User may override.
Note on H8: User may override.
Note on J8: User may override.
Note on K8: - User may override. - Maximum % of use is 10%

## Condensate Drains
No Loss Condensate Drains
No-loss Condensate Drains are controlled by a sensor that monitors the level of condensate and only open when there is a need to drain condensate. They close before compressed air is allowed to escape. The baseline for this measure is a standard condensate drains operated by a solenoid and timer. Energy efficient conditions are systems retrofitted with new No-loss Condensate Drains properly sized for the compressed air system.
Facility Information |  |  | Data Inputs | [8 empty] | Results
Line Items | Building Name | Building Schedule | Drain Orifice Diameter | System Pressure | Air Loss Rate | Compressor Control Type | Ratio of Compressor kW/CFM | Hours Per Year Drain is Open (Default: 146) | Adjustmant Factor | Percent Not Condensate (Default: 0.75) | Number of Drains Installed | Hours of Operation | Coincidence Factor | Annual kWh Savings | Non Coincident kW | Peak kW Savings
1 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
2 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
3 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
4 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
5 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
6 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
7 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
8 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
9 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
10 |  |  |  |  | #N/A |  |  | 146 |  | 0.75 |  | #N/A | #N/A | 0 | 0 | 0
Total | [10 empty] | 0 |  |  | 0 |  | 0
Note on H7: User may override.
Note on I7: User may override value.
Note on J7: User may override Adjustment Factor; accounts for periods when compressor is not running and the system depressurizes due to leaks and operation of time drains.
Note on K7: User may override

## Air Tanks
Air Tanks For Load/No Load Compressors and Modulating Compressors w/Blowdown
This measure protocol applies to the installation of air receivers with pressure/flow controls to load/no load compressors or modulating compressors with blowdown. The baseline equipment is a load/no load compressor or a modulating compressor with blowdown with a 1 gal/cfm storage ratio. The high efficiency equipment is a load/no load compressor or a modulating compressor with blowdown with a minimum storage ratio of 4 gallons of storage per cfm.
Facility Information |  |  | Data Inputs | [7 empty] | Results
Line Item | Building Name | Building Schedule | Rated Compressor Horsepower | Gallons of Storage | Operating CFM level | Conversion Factor (Default: 0.746) | Load Factor (Default 0.92) | Load Reduction (Default 0.10) | Efficiency of Compressor Motor (Default 0.91) | Gallon/CFM Ratio | Hours of Operation | Coincidence Factor | Annual kWh Savings | Non Conicident kW | Peak kW Savings
1 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
2 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
3 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
4 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
5 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
6 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
7 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
8 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
9 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
10 | [5 empty] | 0.746 | 0.92 | 0.1 | 0.91 | 0 | #N/A | #N/A | 0 | 0 | 0
Total | [12 empty] | 0 |  | 0

## Version Log (hidden)
Version Log
Original Author: |  | Ryan Novosedliak | QA/QC Engineer(s):
Primary Developer: |  | Ryan Novosedliak | Senior Engineer Approval:
Version | Date | Reason for Change | Change Description | Contact, Department
0.1 | 2016-04-18 | Creation of Calculator | Creation of Measure Tabs, General Description Tabs, And Lookup Tables | Ryan Novosedliak, Engineering
0.2 | 2016-04-20 | Formulas | Creation of Formulas for measure calculation | Ryan Novosedliak, Engineering
0.3 | 2016-04-27 | Formatting | Formatting of calculator, Populating the Methodolgy and Instruction Page | Ryan Novosedliak, Engineering
1.4.27.16 | 2016-04-27 | Finalizing | Final formatting and labeling. Calculator finished intial creation | Ryan Novosedliak, Engineering
2.16.7.11 | 2016-07-11 | PH3 Change | Updating formatting to comply with phase 3 (Cycling Dryers) | Ryan Novosedliak, Engineering
2.16.7.15 | 2016-07-15 | PH3 Change | Updated formatting to comply with phase 3 (tanks, nozzles, drains) | Ryan Novosedliak, Engineering
2.16.7.18 | 2016-07-18 | PH3 Change | Updated Instructions tab and added project summary tab | Ryan Novosedliak, Engineering
3 | 2016-07-18 | Finalization for PH3 | calculator Finalized for final use in phase 3 | Ryan Novosedliak, Engineering
3.17.4.26 | 2017-04-26 | Add Comp Air | Add table for compressor replacement (2010 OH TRM) | Ryan Novosedliak, Engineering
3.17.4.27 | 2017-04-27 | Final for Test | Finalized for testing for approval | Ryan Novosedliak, Engineering
3.17.5.16 | 2017-05-16 | ADM Revisions | Added 150 HP limit to dryers. Added 4 gal/cfm ratio | Ryan Novosedliak, Engineering
4 | 2017-05-16 | Submission | Submission to FE for program use | Ryan Novosedliak, Engineering
4.1 | 2017-06-09 | Calculator Update | Calculator updated based on ADM findings | Ryan Novosedliak, Engineering
4.2 | 2017-06-12 | Calculator Update | CF for single shify updated to .24 | Ryan Novosedliak, Engineering
4.3 | 2017-06-29 | Calculator Update | Formatting Update | Ryan Novosedliak, Engineering
4.4 | 2020-07-20 | Calculator Update | Removed VFD Compressor as it refrences Phase 4 TRM. Updated for CR Use | Ryan Novosedliak, Engineering
5 | 2021-05-21 | Calculator Update | Revise all calculations to Phase 4 TRM, rebranded any references to CSP, phone number, email, and TRM versions | Cliff Zimmerman, Franklin Engineering
5 | 2021-06-04 | Calculator Update | Revised to include a peak kW with custom hours and custom CF calculation (defaults to TRM if not completed). | Ashley Faircloth, Franklin Engineering
5.1 | 2021-06-15 | Calculator Update | Updated language for instructions on air compressor, removed "total number of compressors" and edited Compressor horsepower to total horsepower on Cycling dryer. Removed number of compressors column on Air Nozzle, Updated to reflect overridable inputs on air nozzle, added eligibility clarification to air nozzle, removed number of compressors from condensate drain, allow user override on condensate drains, removed number of compressors from air tanks, added note for minimum requirements and that inlet modulation with blowdown is eligible to air tanks. | Sara Aaserud, Franklin Energy

## Lookup Tables (hidden)
Adjustmant Factor |  | Baseline Nozzle Mass Flow |  | Average Compressor kW/CFM |  | Average Air Loss Rates
Building Schedule | AF | Nozzle Diameter | Air Mass Flow | Compressor Control Type | Average Compressor kW/CFM | Pressure (psig) | Orifice Diameter (inches)
Single Shift (8/5) | 0.62 | 1/8" | 21 | Modulating w/ Blowdown | 0.32 |  | 0.015625 | 0.03125 | 0.0625 | 0.125 | 0.25 | 0.375
2-Shift (16/5) | 0.74 | 1/4" | 58 | Load/No Load w/ 1 gal/CFM Storage | 0.32 | 70 | 0.29 | 1.16 | 4.66 | 18.62 | 74.4 | 167.8
3-Shift (24/5) | 0.86 |  |  | Load/No Load w/ 3 gal/CFM Storage | 0.3 | 80 | 0.32 | 1.26 | 5.24 | 20.76 | 83.1 | 187.2
4-Shift (24/7) | 0.97 | Air Entraining Nozzle Mass Flow |  | Load/No Load w/ 5 gal/CFM Storage | 0.28 | 90 | 0.36 | 1.46 | 5.72 | 23.1 | 92 | 206.6
|  | Nozzle Diameter | Air Mass Flow | Variable Speed w/ Unloading | 0.23 | 95 | 0.38 | 1.51 | 6.02 | 24.16 | 96.5 | 216.8
Compressor Hours |  | 1/8" | 6 | Unknown | 0.27 | 100 | 0.4 | 1.55 | 6.31 | 25.22 | 100.9 | 227
Building Schedule | Hours | 1/4" | 11 |  |  | 105 | 0.42 | 1.63 | 6.58 | 26.31 | 105.2 | 236.7
Single Shift (8/5) | 1976 |  |  |  |  | 110 | 0.43 | 1.71 | 6.85 | 27.39 | 109.4 | 246.4
2-Shift (16/5) | 3952 | Control Energy Savings Factor |  |  |  | 115 | 0.45 | 1.78 | 7.12 | 28.48 | 113.7 | 256.1
3-Shift (24/5) | 5928 | Control | ESF |  |  | 120 | 0.46 | 1.86 | 7.39 | 29.56 | 117.9 | 265.8
4-Shift (24/7) | 8320 | Load/No Load | 0.1 |  |  | 125 | 0.48 | 1.94 | 7.66 | 30.65 | 122.2 | 275.5
|  | Variable Displacement | 0.17
|  | Variable Frequency Drive | 0.26 |  |  | VLOOKUP1 | 0
Compressor CF | [5 empty] | VLOOKUP2 | 0
Building Schedule | % |  |  |  |  | VLOOKUP3 | 0
Single Shift (8/5) | 0.24 |  |  |  |  | VLOOKUP4 | 0
2-Shift (16/5) | 0.95 |  |  |  |  | VLOOKUP5 | 0
3-Shift (24/5) | 0.95 |  |  |  |  | VLOOKUP6 | 0
4-Shift (24/7) | 0.95 |  |  |  |  | VLOOKUP7 | 0
[6 empty] | VLOOKUP8 | 0
[6 empty] | VLOOKUP9 | 0
[6 empty] | VLOOKUP0 | 0
12:00am
1:00am
2:00am
3:00am
4:00am
5:00am
6:00am
7:00am
8:00am
9:00am
10:00am
11:00am
12:00pm
1:00pm
2:00pm
3:00pm
4:00pm
5:00pm
6:00pm
7:00pm
8:00pm
9:00pm
10:00pm
11:00pm